## DB-CPV-B1
CEASERS PALACE VILLA
LOAD DISTRIBUTION SCHEDULE | [26 empty] | Lighting Load | Small Power | Kitchen Loads | Water Heater | FCU | Spare
Document Number: VILLA BASEMENT 1
PROJECT: | CEASERS PALACE VILLA | [20 empty] | LOCATION : ELECTRICAL ROOM
DB No: | DB-CPV-B1
Fed From: | LH-B1-SR1-SMDB-001 | [22 empty] | PAGE-1
RATING | RATING | SR. | CKT | MCB | CKT | ECC | ROOM/AREA | CONNECTED LOADS/POINTS | [13 empty] | WATTS | LOAD PER CKT. |  |  | REMARKS
OF | OF | NO. | NO. | RTG | WIRE | WIRE | [15 empty] | /UNIT | KILO WATTS
INCOMER | ELCB |  |  |  | SIZE | SIZE |  | LTG. | EX. | FLEX | SH. | 13A | 32A | W/H | W/M | D/W | CCU | W | 15A | FCU | MISC |  | R | Y | B
|  |  |  | Amp. | mm2 | mm2 |  |  | FAN | O/L | S/O | S/O | S/O |  |  |  |  | A/C | SS0
63A TP ISOLATOR |  | 1 | 1R | 10 | 2.5 | 2.5 | MASTER BEDROOM L/L | 9 | [13 empty] | 15&100 | 0.22 |  |  | LIGHTING | 0.22
| 40A | 2 | 1Y | 10 | 2.5 | 2.5 | MASTER BATHROOM | 11 | [13 empty] | 10 |  | 0.11 |  | LIGHTING | 0.11
| 4P | 3 | 1B | 10 | 2.5 | 2.5 | CORRIDOR | 12 | [13 empty] | 15&5 |  |  | 0.21 | LIGHTING | 0.21
| 100mA | 4 | 2R | 10 | 2.5 | 2.5 | POWDER ROOM | 9 | [13 empty] | 10 | 0.09 |  |  | LIGHTING | 0.09
|  | 5 | 2Y | 10 | 2.5 | 2.5 | MASTER BATHROOM(LED LIGTHS IN MTRS) | 10.8 | [13 empty] | 4.5 |  | 0.0486 |  | LIGHTING | 0.0486
|  | 6 | 2B | 10 | 2.5 | 2.5 | DINING | 7 | [13 empty] | 15&5 |  |  | 0.675 | LIGHTING | 0.675
|  | 7 | 3R | 10 | 2.5 | 2.5 | CORRIDOR | 15 | [13 empty] | 15 & 5 | 0.26 |  |  | LIGHTING | 0.26
| 40A | 8 | 3Y | 10 | 2.5 | 2.5 | MEDIA ROOM | 7 | [13 empty] | 15 & 5 |  | 0.15 |  | LIGHTING | 0.15
| 4P | 9 | 3B | 10 | 2.5 | 2.5 | KITCHEN & BAR | 11 | [13 empty] | 15&5 |  |  | 0.77 | LIGHTING | 0.77
| 100mA | 10 | 4R | 10 | 2.5 | 2.5 | LIVING AREA | 3 | [13 empty] | 15&100 | 0.15 |  |  | LIGHTING | 0.15
|  | 11 | 4Y | 10 | 2.5 | 2.5 | DRIVER/MAIDS BATH | 4 | [13 empty] | 15 |  | 0.06 |  | LIGHTING | 0.06
|  | 12 | 4B | 10 | 4 | 4 | LANDSCAPE | 22 | [13 empty] | 25 |  |  | 0.55 | LIGHTING | 0.55
|  | 13 | 5R | 10 | 4 | 4 | LANDSCAPE | 28 | [13 empty] | 25 | 0.7 |  |  | LIGHTING | 0.7
| 40A | 14 | 5Y | 10 | 4 | 4 | LANDSCAPE | 33 | [13 empty] | 25 - 100 |  | 0.9 |  | LIGHTING | 0.9
| 4P | 15 | 5B | 10 | 4 | 4 | LANDSCAPE | 19 | [13 empty] | 25 |  |  | 0.475 | LIGHTING | 0.475
| 100mA | 16 | 6R | 10 | 4 | 4 | LANDSCAPE | 22 | [13 empty] | 25 | 0.55 |  |  | LIGHTING | 0.55
|  | 17 | 6Y | 10 | 2.5 | 2.5 | MASTER BATHROOM | 2 | [13 empty] | 25 |  | 0.05 |  | LIGHTING | 0.05
|  | 18 | 6B | 10 | 2.5 | 2.5 | LIFT SHAFT | 2 | [13 empty] | 21.3 |  |  | 0.0426 | LIGHTING | 0.0426 |  |  |  |  | 0.0426
|  | 19 | 7R | 32 | 4 | 4 | MASTER BEDROOM |  |  |  |  | 9 | [9 empty] | 200 | 1.8 |  |  | RING CKT |  | 1.8
| 40A | 20 | 7Y | 20 |  |  | SPARE | [13 empty] | 1 | 200 |  | 0.2 |  | SPARE | [5 empty] | 0.2
| 4P | 21 | 7B | 20 |  |  | SPARE | [13 empty] | 1 | 200 |  |  | 0.2 | SPARE | [5 empty] | 0.2
| 30mA | 22 | 8R | 32 | 4 | 4 | MASTER BEDROOM |  |  |  | 3 | 3 | [9 empty] | 200 | 1.2 |  |  | RING CKT |  | 1.2
|  | 23 | 8Y | 32 | 4 | 4 | MEDIA ROOM |  |  |  |  | 6 | [9 empty] | 200 |  | 1.2 |  | RING CKT |  | 1.2
|  | 24 | 8B | 32 | 4 | 4 | LIVING AREA |  |  |  |  | 9 | [9 empty] | 200 |  |  | 1.8 | RING CKT |  | 1.8
[27 empty] | 6.0112 | 6 | 0 | 0 | 0 | 0.4426
LTG.=LIGHTING,EX. FAN = EXHAUST FAN, S/O=SOCKET OUTLET,SH. S/O = SHAVER SOCKET OUTLET, W/H = WATER HEATER, H/D = HAND DRYER | [22 empty] | CONT…2
D/W=DISH WASHER, FCU=FAN COIL UNIT, CCU = COOKER CONTROL UNIT, W = WINDOW TYPE A/C & S = SPLIT TYPE A/C
CEASERS PALACE VILLA
LOAD DISTRIBUTION SCHEDULE | [26 empty] | Lighting Load | Small Power | Kitchen Loads | Water Heater | FCU | Spare
Document Number: VILLA BASEMENT 1
PROJECT: | CEASERS PALACE VILLA | [20 empty] | LOCATION : ELECTRICAL ROOM
DB No: | DB-CPV-B1
Fed From: | LH-B1-SR1-SMDB-001 | [22 empty] | PAGE- 2
RATING | RATING | SR. | CKT | MCB | CKT | ECC | ROOM/AREA | CONNECTED LOADS/POINTS | [13 empty] | WATTS | LOAD PER CKT. |  |  | REMARKS
OF | OF | NO. | NO. | RTG | WIRE | WIRE | [15 empty] | /UNIT | KILO WATTS
INCOMER | ELCB |  |  |  | SIZE | SIZE |  | LTG. | EX. | FLEX | SH. | 13A | 32A | W/H | W/M | D/W | CCU | W | 15A | FCU | MISC |  | R | Y | B
|  |  |  | Amp. | mm2 | mm2 |  |  | FAN | O/L | S/O | S/O | S/O |  |  |  |  | A/C | SS0
63A TP ISOLATOR |  | 25 | 9R | 32 | 4 | 4 | MASTER BEDROOM |  |  |  |  | 7 | [9 empty] | 200 | 1.4 |  |  | RING CKT |  | 1.4
| 40A | 26 | 9Y | 32 | 4 | 4 | MEDIA ROOM |  |  |  |  | 8 | [9 empty] | 200 |  | 1.6 |  | RING CKT |  | 1.6
| 4P | 27 | 9B | 20 |  |  | SPARE | [17 empty] | 0 | SPARE | [5 empty] | 0
| 30mA | 28 | 10R | 32 | 4 | 4 | EXTERNAL MASTER BATHROOM |  |  |  |  | 1 | [9 empty] | 200 | 0.2 |  |  |  |  | 0.2
|  | 29 | 10Y | 32 | 4 | 4 | MAID/DRIVER ROOM |  |  |  |  | 6 | [9 empty] | 200 |  | 1.2 |  | RING CKT |  | 1.2
|  | 30 | 10B | 32 | 4 | 4 | CORRIDOR |  |  |  |  | 3 | [9 empty] | 200 |  |  | 0.6 | RING CKT |  | 0.6
|  | 31 | 11R | 20 | 4 | 4 | MASTER BATHROOM |  |  |  |  | 1 | [9 empty] | 100 | 0.1 |  |  |  |  | 0.1
| 40A | 32 | 11Y |  |  |  | SPACE | [16 empty] | 0 | [6 empty] | 0
| 4P | 33 | 11B | 20 | 4 | 4 | LIVING ROOM |  |  |  |  | 4 | [9 empty] | 200 |  |  | 0.8 | RING CKT |  | 0.8
| 30mA | 34 | 12R | 32 | 4 | 4 | DINING AREA |  |  |  |  | 7 | [9 empty] | 200 | 1.4 |  |  |  |  | 1.4
|  | 35 | 12Y | 20 |  |  | SPARE | [13 empty] | 1 | 50 |  | 0.05 | [7 empty] | 0.05
|  | 36 | 12B | 20 | 4 | 4 | LANDSCAPE |  |  |  |  | 1 | [9 empty] | 500 |  |  | 0.5 | DCU |  | 0.5
|  | 37 | 13R | 20 | 4 | 4 | CORRIDOR | [13 empty] | 1 | 550 | 0.55 |  |  | EXTRACT FANS |  | 0.55
| 40A | 38 | 13Y | 25 | 6 | 6 | KITCHEN | [13 empty] | 1 | 2400 |  | 2.4 |  | GRIDDLE (SWK 7) |  |  | 2.4
| 4P | 39 | 13B | 20 |  |  | SPARE | [13 empty] | 1 | 130 |  |  | 0.13 | SPARE | [5 empty] | 0.13
| 30mA | 40 | 14R | 20 | 4 | 4 | CORRIDOR | [13 empty] | 1 | 255 | 0.255 |  |  | EXTRACT FANS |  | 0.255
|  | 41 | 14Y | 20 |  |  | SPARE | [13 empty] | 1 | 400 |  | 0.4 |  | SPARE | [5 empty] | 0.4
|  | 42 | 14B | 20 |  |  | SPARE | [13 empty] | 1 | 305 |  |  | 0.305 | SPARE | [5 empty] | 0.305
|  | 43 | 15R | 20 | 4 | 4 | LANDSCAPE |  |  |  |  | 1 | [9 empty] | 100 | 0.1 |  |  | DCU | [5 empty] | 0.1
| 40A | 44 | 15Y | 20 |  |  | SPARE | [13 empty] | 1 | 200 |  | 0.2 |  | SPARE | [5 empty] | 0.2
| 4P | 45 | 15B | 32 | 4 | 4 | LANDSCAPE |  |  |  |  | 6 | [9 empty] | 200 |  |  | 1.2 | RING CKT |  | 1.2
| 30mA | 46 | 16R | 20 |  |  | SPARE | [13 empty] | 1 | 600 | 0.6 |  |  | SPARE | [5 empty] | 0.6
|  | 47 | 16Y | 20 |  |  | SPARE | [13 empty] | 1 | 600 |  | 0.6 |  | SPARE | [5 empty] | 0.6
|  | 48 | 16B | 20 | 4 | 4 | LANDSCAPE | [5 empty] | 1 | [8 empty] | 1500 |  |  | 1.5 |  |  | 1.5
[27 empty] | 0 | 11.305 | 2.4 | 0 | 0 | 2.385
LTG.=LIGHTING,EX. FAN = EXHAUST FAN, S/O=SOCKET OUTLET,SH. S/O = SHAVER SOCKET OUTLET, W/H = WATER HEATER, H/D = HAND DRYER | [22 empty] | CONT…3
D/W=DISH WASHER, FCU=FAN COIL UNIT, CCU = COOKER CONTROL UNIT, W = WINDOW TYPE A/C & S = SPLIT TYPE A/C
CEASERS PALACE VILLA
LOAD DISTRIBUTION SCHEDULE | [26 empty] | Lighting Load | Small Power | Kitchen Loads | Water Heater | FCU | Spare
Document Number: VILLA BASEMENT 1
PROJECT: | CEASERS PALACE VILLA | [20 empty] | LOCATION : ELECTRICAL ROOM
DB No: | DB-CPV-B1
Fed From: | LH-B1-SR1-SMDB-001 | [22 empty] | PAGE- 3
RATING | RATING | SR. | CKT | MCB | CKT | ECC | ROOM/AREA | CONNECTED LOADS/POINTS | [13 empty] | WATTS | LOAD PER CKT. |  |  | REMARKS
OF | OF | NO. | NO. | RTG | WIRE | WIRE | [15 empty] | /UNIT | KILO WATTS
INCOMER | ELCB |  |  |  | SIZE | SIZE |  | LTG. | EX. | FLEX | SH. | 13A | 32A | W/H | W/M | D/W | CCU | W | 15A | FCU | MISC |  | R | Y | B
|  |  |  | Amp. | mm2 | mm2 |  |  | FAN | O/L | S/O | S/O | S/O |  |  |  |  | A/C | SS0
63A TP ISOLATOR |  | 49 | 17R | 10 | 2.5 | 2.5 | STAIRS | 20 | [13 empty] | 5 | 0.1 |  |  | LIGHTING | 0.1 |  |  |  |  | 0.1
| 40A | 50 | 17Y | 20 | 4 | 4 | MAID/DRIVER ROOM | [12 empty] | 1 |  | 300 |  | 0.3 |  | A/C |  |  |  |  | 0.3
| 4P | 51 | 17B | 10 |  |  | SPARE | [13 empty] | 1 | 500 |  |  | 0.5 | SPARE | [5 empty] | 0.5
| 100mA | 52 | 18R | 20 | 4 | 4 | MASTER BEDROOM | [12 empty] | 1 |  | 300 | 0.3 |  |  | A/C |  |  |  |  | 0.3
|  | 53 | 18Y | 20 | 4 | 4 | MAID/DRIVER ROOM | [12 empty] | 1 |  | 300 |  | 0.3 |  | A/C |  |  |  |  | 0.3
|  | 54 | 18B |  |  |  | SPACE | [17 empty] | 0
CABLE SIZE : 1x4C ..50...mm2 XLPE/SWA/LSOH+ 1x1C …25..mm2 CU PVC-ECC. | [13 empty] | LOAD PER PHASE (KW) | [8 empty] | 9.975 | 9.7686 | 10.2576 |  | 0.1 | 0 | 0 | 0 | 0.9 | 0.6 | 30.1438 | 23.635
LTG.=LIGHTING,EX. FAN = EXHAUST FAN, S/O=SOCKET OUTLET,SH. S/O = SHAVER SOCKET OUTLET, W/H = WATER HEATER, H/D = HAND DRYER, D/W=DISH WASHER | [21 empty] | TOTAL LOAD = |  |  | 30.0012 | KW
FCU=FAN COIL UNIT, CCU = COOKER CONTROL UNIT, W = WINDOW TYPE A/C & S = SPLIT TYPE A/C | [21 empty] | DEMAND LOAD = |  |  | 23.635 | KW
[27 empty] | 6.1112 | 17.305 | 2.4 | 0 | 0.9 | 3.4276 | 30.1438 | TCL
[27 empty] | 0.8 | 0.8 | 0.6 | 0.8 | 0.8 | 0.8 | 0.78408 | DF
[27 empty] | 4.889 | 13.844 | 1.44 | 0 | 0.72 | 2.7421 | 23.635 | MDL

## DB-CPV-MAJ
CEASERS PALACE VILLA
LOAD DISTRIBUTION SCHEDULE | [26 empty] | Lighting Load | Small Power | Kitchen Loads | Water Heater | FCU | Spare
Document Number: MAJLIS AREA
PROJECT: | CEASERS PALACE VILLA | [20 empty] | LOCATION : MAJLIS
DB No: | DB-CPV-MAJ
Fed From: | LH-B1-SR1-SMDB-001 | [22 empty] | PAGE-1
RATING | RATING | SR. | CKT | MCB | CKT | ECC | ROOM/AREA | CONNECTED LOADS/POINTS | [13 empty] | WATTS | LOAD PER CKT. |  |  | REMARKS
OF | OF | NO. | NO. | RTG | WIRE | WIRE | [15 empty] | /UNIT | KILO WATTS
INCOMER | ELCB |  |  |  | SIZE | SIZE |  | LTG. | EX. | FLEX | SH. | 13A | 32A | W/H | W/M | D/W | 15A | W | S | FCU | MISC |  | R | Y | B
|  |  |  | Amp. | mm2 | mm2 |  |  | FAN | O/L | S/O | S/O | S/O |  |  |  | S/O | A/C | A/C
100A TP ISOLATOR |  | 1 | 1R | 10 | 4 | 4 | LANDSCAPE | 22 | [13 empty] | 25 | 0.55 |  |  | LIGHTING | 0.55
| 40A | 2 | 1Y | 10 | 4 | 4 | LANDSCAPE | 12 | [13 empty] | 30 |  | 0.36 |  | LIGHTING | 0.36
| 4P | 3 | 1B | 10 | 2.5 | 2.5 | MAJLIS CHANDELIER | 1 | [13 empty] | 500 |  |  | 0.5 | LIGHTING | 0.5
| 100mA | 4 | 2R | 10 | 2.5 | 2.5 | LANDSCAPE MAJLIS | 14 | [13 empty] | 25 | 0.35 |  |  | LIGHTING | 0.35
|  | 5 | 2Y | 10 | 2.5 | 2.5 | LANDSCAPE MAJLIS | 14 | [13 empty] | 25 |  | 0.35 |  | LIGHTING | 0.35
|  | 6 | 2B | 10 | 2.5 | 2.5 | MAJLIS CHANDELIER | 1 | [13 empty] | 500 |  |  | 0.5 | LIGHTING | 0.5
|  | 7 | 3R | 10 | 2.5 | 2.5 | MAJLIS | 14 | [13 empty] | 25 | 0.35 |  |  | LIGHTING | 0.35
| 40A | 8 | 3Y | 10 | 2.5 | 2.5 | POWDER & WASHROOMS | 9 | [13 empty] | 25 |  | 0.225 |  | LIGHTING | 0.225
| 4P | 9 | 3B | 10 | 2.5 | 2.5 | KITCHEN | 6 | [13 empty] | 25 |  |  | 0.15 | LIGHTING | 0.15
| 100mA | 10 | 4R | 10 | 2.5 | 2.5 | MAJLIS (Meters) | 15 | [13 empty] | 10 | 0.15 |  |  | LIGHTING | 0.15
|  | 11 | 4Y | 10 | 2.5 | 2.5 | GYM | 2 | [13 empty] | 100 |  | 0.2 |  | LIGHTING | 0.2
|  | 12 | 4B | 10 | 2.5 | 2.5 | MAJLIS CHANDELIER | 1 | [12 empty] | 1 | 500 |  |  | 1 | LIGHTI NG | [5 empty] | 1
|  | 13 | 5R | 32 | 4 | 4 | LANDSCAPE |  |  |  |  | 10 | [9 empty] | 200 | 2 |  |  | RING CKT |  | 2
| 40A | 14 | 5Y | 20 | 4 | 4 | LANDSCAPE | [5 empty] | 1 | [8 empty] | 1500 |  | 1.5 |  |  |  | 1.5
| 4P | 15 | 5B | 20 | 4 | 4 | LANDSCAPE | [5 empty] | 1 | [8 empty] | 1500 |  |  | 1.5 |  |  | 1.5
| 100mA | 16 | 6R | 20 | 4 | 4 | LANDSCAPE | [13 empty] | 1 | 500 | 0.5 |  |  | GATE BARRIER |  | 0.5
|  | 17 | 6Y | 20 | 4 | 4 | BAR |  |  |  |  | 2 | [9 empty] | 400 |  | 0.8 |  | ICE CUBER (MBA 6) & BOTTLE DISPLAY (MBA 7) |  |  | 0.8 |  |  |  |  | 0.8
|  | 18 | 6B | 32 | 6 | 6 | BAR | [13 empty] | 1 | 3300 |  |  | 3.3 | GLASS WASHER (MBA 4) |  |  | 3.3 |  |  |  |  | 3.3
|  | 19 | 7R | 32 | 4 | 4 | MAJLIS |  |  |  |  | 6 | [9 empty] | 200 | 1.2 |  |  | RING CKT |  | 1.2
| 40A | 20 | 7Y | 32 | 4 | 4 | GYM / CHANGING ROOM |  |  |  |  | 9 | [9 empty] | 200 |  | 1.8 |  | RING CKT |  | 1.8
| 4P | 21 | 7B | 32 | 4 | 4 | PANTRY |  |  |  |  | 7 | [9 empty] | 200 |  |  | 1.4 | RING CKT |  |  | 1.4
| 30mA | 22 | 8R | 32 | 4 | 4 | MAJLIS |  |  |  |  | 6 | [9 empty] | 200 | 1.2 |  |  | RING CKT |  | 1.2
|  | 23 | 8Y | 20 | 4 | 4 | PANTRY | [6 empty] | 1 | [7 empty] | 1200 |  | 1.2 |  | WATER HEATER |  |  | 1.2
|  | 24 | 8B | 20 | 4 | 4 | GYM |  |  |  |  | 1 | [9 empty] | 200 |  |  | 0.2 |  |  | 0.2
[27 empty] | 3.685 | 9.9 | 6.7 | 0 | 0 | 1
LTG.=LIGHTING,EX. FAN = EXHAUST FAN, S/O=SOCKET OUTLET,SH. S/O = SHAVER SOCKET OUTLET, W/H = WATER HEATER, H/D = HAND DRYER | [22 empty] | CONT…2
D/W=DISH WASHER, FCU=FAN COIL UNIT, CCU = COOKER CONTROL UNIT, W = WINDOW TYPE A/C & S = SPLIT TYPE A/C
CEASERS PALACE VILLA
LOAD DISTRIBUTION SCHEDULE | [26 empty] | Lighting Load | Small Power | Kitchen Loads | Water Heater | FCU | Spare
Document Number: MAJLIS AREA
PROJECT: | CEASERS PALACE VILLA | [20 empty] | LOCATION : ELECTRICAL ROOM
DB No: | DB-CPV-MAJ
Fed From: | LH-B1-SR1-SMDB-001 | [22 empty] | PAGE- 2
RATING | RATING | SR. | CKT | MCB | CKT | ECC | ROOM/AREA | CONNECTED LOADS/POINTS | [13 empty] | WATTS | LOAD PER CKT. |  |  | REMARKS
OF | OF | NO. | NO. | RTG | WIRE | WIRE | [15 empty] | /UNIT | KILO WATTS
INCOMER | ELCB |  |  |  | SIZE | SIZE |  | LTG. | EX. | FLEX | SH. | 13A | 32A | W/H | W/M | D/W | 15A | W | S | FCU | MISC |  | R | Y | B
|  |  |  | Amp. | mm2 | mm2 |  |  | FAN | O/L | S/O | S/O | S/O |  |  |  | S/O | A/C | A/C
100A TP ISOLATOR |  | 25 | 9R | 32 |  |  | SPARE | [13 empty] | 1 | 2500 | 2.5 | [8 empty] | 2.5
| 40A | 26 | 9Y | 32 | 6 | 6 | PANTRY | [9 empty] | 1 |  |  |  |  | 3000 |  | 3 |  | OVEN (MPA 8) |  |  | 3
| 4P | 27 | 9B | 20 | 4 | 4 | PANTRY |  |  |  |  | 1 | [9 empty] | 240 |  |  | 0.24 | REFRIGERATOR (MPA 9) |  |  | 0.24
| 30mA | 28 | 10R | 20 | 4 | 4 | WASH ROOM | [6 empty] | 1 | [7 empty] | 1200 | 1.2 |  |  | WATER HEATER |  |  |  | 1.2
|  | 29 | 10Y | 20 |  |  | SPARE | [13 empty] | 1 | 800 |  | 0.8 |  | SPARE | [5 empty] | 0.8
|  | 30 | 10B | 32 | 6 | 6 | PANTRY | [8 empty] | 1 | [5 empty] | 3300 |  |  | 3.3 | DISHWASHER (MPA 3) |  |  | 3.3
|  | 31 | 11R | 20 | 4 | 4 | CHANGING ROOM | [13 empty] | 1 | 500 | 0.5 |  |  | ERV-01 |  | 0.5
| 40A | 32 | 11Y | 20 | 4 | 4 | PANTRY | [13 empty] | 1 | 350 |  | 0.35 |  | HOOD (MPA 7) |  |  | 0.35
| 4P | 33 | 11B | 20 |  |  | SPARE | [13 empty] | 1 | 1000 |  |  | 1 | [5 empty] | 1
| 30mA | 34 | 12R | 20 | 4 | 4 | PANTRY |  |  |  |  | 1 | [9 empty] | 200 | 0.2 |  |  | EXISTING (MPA 10) |  |  | 0.2
|  | 35 | 12Y | 20 |  |  | SPARE | [13 empty] | 1 | 200 |  | 0.2 |  | SPARE | [5 empty] | 0.2
|  | 36 | 12B | 20 |  |  | SPARE | [13 empty] | 1 | 200 |  |  | 0.2 | SPARE | [5 empty] | 0.2
|  | 37 | 13R | 20 | 4 | 4 | PANTRY |  |  |  |  | 1 | [9 empty] | 200 | 0.2 |  |  | EXISTING (MPA 10) |  |  | 0.2
| 40A | 38 | 13Y | 32 | 4 | 4 | PANTRY |  |  |  |  | 7 | [9 empty] | 200 |  | 1.4 |  | RING CKT |  |  | 1.4
| 4P | 39 | 13B | 20 | 4 | 4 | PANTRY |  |  |  |  | 1 | [9 empty] | 200 |  |  | 0.2 | EXISTING (MPA 10) |  |  | 0.2
| 30mA | 40 | 14R | 20 | 4 | 4 | PANTRY |  |  |  |  | 1 | [9 empty] | 200 | 0.2 |  |  | EXISTING (MPA 10) |  |  | 0.2
|  | 41 | 14Y | 20 | 4 | 4 | PANTRY |  |  |  |  | 2 | [9 empty] | 200 |  | 0.4 |  | BOTTLE DISPLAY (MBA 7) |  |  | 0.4
|  | 42 | 14B | 20 | 4 | 4 | PANTRY |  |  |  |  | 1 | [9 empty] | 200 |  |  | 0.2 | EXISTING (MPA 10) |  |  | 0.2
|  | 43 | 15R | 32 | 4 | 4 | MAJLIS |  |  |  |  | 6 | [9 empty] | 200 | 1.2 |  |  | RING CKT |  | 1.2
| 40A | 44 | 15Y | 20 |  |  | SPARE | [13 empty] | 1 | 1000 |  | 1 |  | SPARE | [5 empty] | 1
| 4P | 45 | 15B | 20 |  |  | SPARE | [13 empty] | 1 | 200 |  |  | 0.2 | SPARE | [5 empty] | 0.2
| 30mA | 46 | 16R | 20 | 4 | 4 | PUMP ROOM |  |  |  |  | 2 | [9 empty] | 200 | 0.4 |  |  | RING CKT |  | 0.4
|  | 47 | 16Y | 20 | 4 | 4 | LANDSCAPE |  |  |  |  | 1 | [9 empty] | 200 |  | 0.2 |  | DCU |  | 0.2
|  | 48 | 16B | 20 | 4 | 4 | TOILET |  |  |  | 1 | [10 empty] | 100 |  |  | 0.1 |  |  | 0.1
[27 empty] | 0 | 2.4 | 9.69 | 1.2 | 1 | 4.9
LTG.=LIGHTING,EX. FAN = EXHAUST FAN, S/O=SOCKET OUTLET,SH. S/O = SHAVER SOCKET OUTLET, W/H = WATER HEATER, H/D = HAND DRYER | [22 empty] | CONT…2
D/W=DISH WASHER, FCU=FAN COIL UNIT, CCU = COOKER CONTROL UNIT, W = WINDOW TYPE A/C & S = SPLIT TYPE A/C
CEASERS PALACE VILLA
LOAD DISTRIBUTION SCHEDULE | [26 empty] | Lighting Load | Small Power | Kitchen Loads | Water Heater | FCU | Spare
Document Number: MAJLIS AREA
PROJECT: | CEASERS PALACE VILLA | [20 empty] | LOCATION : ELECTRICAL ROOM
DB No: | DB-CPV-MAJ
Fed From: | LH-B1-SR1-SMDB-001 | [22 empty] | PAGE- 3
RATING | RATING | SR. | CKT | MCB | CKT | ECC | ROOM/AREA | CONNECTED LOADS/POINTS | [13 empty] | WATTS | LOAD PER CKT. |  |  | REMARKS
OF | OF | NO. | NO. | RTG | WIRE | WIRE | [15 empty] | /UNIT | KILO WATTS
INCOMER | ELCB |  |  |  | SIZE | SIZE |  | LTG. | EX. | FLEX | SH. | 13A | 32A | W/H | W/M | D/W | 15A | W | S | FCU | MISC |  | R | Y | B
|  |  |  | Amp. | mm2 | mm2 |  |  | FAN | O/L | S/O | S/O | S/O |  |  |  | S/O | A/C | A/C
100A TP ISOLATOR |  | 49 | 17R | 20 | 4 | 4 | PUMP ROOM | [12 empty] | 1 |  | 300 | 0.3 |  |  | A/C |  |  |  |  | 0.3
| 40A | 50 | 17Y | 20 |  |  | SPARE | [13 empty] | 1 | 900 |  | 0.9 | [7 empty] | 0.9
| 4P | 51 | 17B | 20 | 4 | 4 | PANTRY | [12 empty] | 1 |  | 300 |  |  | 0.3 | A/C |  |  |  |  | 0.3
| 100mA | 52 | 18R | 20 | 4 | 4 | CHANGING ROOM | [12 empty] | 1 |  | 300 | 0.3 |  |  | A/C |  |  |  |  | 0.3
|  | 53 | 18Y | 10 |  |  | SPARE | [13 empty] | 1 | 800 |  | 0.8 | [7 empty] | 0.8
|  | 54 | 18B | 20 | 4 | 4 | PANTRY | [12 empty] | 1 |  | 300 |  |  | 0.3 | A/C |  |  |  |  | 0.3
CABLE SIZE : 1x4C ..95....mm2 XLPE/SWA/LSOH+ 1x1C …50...mm2 CU PVC-ECC. | [13 empty] | LOAD PER PHASE (KW) | [8 empty] | 13.3 | 15.485 | 14.59 |  | 0 | 0 | 0 | 0 | 1.2 | 1.7 | 43.375 | 31.422
LTG.=LIGHTING,EX. FAN = EXHAUST FAN, S/O=SOCKET OUTLET,SH. S/O = SHAVER SOCKET OUTLET, W/H = WATER HEATER, H/D = HAND DRYER, D/W=DISH WASHER | [21 empty] | TOTAL LOAD = |  |  | 43.375 | KW
FCU=FAN COIL UNIT, CCU = COOKER CONTROL UNIT, W = WINDOW TYPE A/C & S = SPLIT TYPE A/C | [21 empty] | DEMAND LOAD = |  |  | 31.422 | KW
[27 empty] | 3.685 | 12.3 | 16.39 | 1.2 | 2.2 | 7.6 | 43.375 | TCL
[27 empty] | 0.8 | 0.8 | 0.6 | 0.8 | 0.8 | 0.8 | 0.72443 | DF
[27 empty] | 2.948 | 9.84 | 9.834 | 0.96 | 1.76 | 6.08 | 31.422 | MDL

## DB-CPV-KIT
CEASERS PALACE VILLA
LOAD DISTRIBUTION SCHEDULE | [26 empty] | Lighting Load | Small Power | Kitchen Loads | Water Heater | FCU | Spare
Document Number: VILLA BASEMENT 1
PROJECT: | CEASERS PALACE VILLA | [20 empty] | LOCATION : ELECTRICAL ROOM
DB No: | DB-CPV-KIT
Fed From: | LH-B1-SR1-SMDB-001 | [22 empty] | PAGE-1
RATING | RATING | SR. | CKT | MCB | CKT | ECC | ROOM/AREA | CONNECTED LOADS/POINTS | [13 empty] | WATTS | LOAD PER CKT. |  |  | REMARKS
OF | OF | NO. | NO. | RTG | WIRE | WIRE | [15 empty] | /UNIT | KILO WATTS
INCOMER | ELCB |  |  |  | SIZE | SIZE |  | LTG. | EX. | FLEX | SH. | 13A | 32A | W/H | W/M | D/W | 15A | W | S | FCU | MISC |  | R | Y | B
|  |  |  | Amp. | mm2 | mm2 |  |  | FAN | O/L | S/O | S/O | S/O |  |  |  | S/O | A/C | A/C
80A TP ISOLATOR |  | 1 | 1R | 20 | 4 | 4 | KITCHEN |  |  |  |  | 2 | [9 empty] | 200 | 0.4 |  |  | EXISTING (SPA 7) |  |  | 0.4
| 40A | 2 | 1Y | 20 | 4 | 4 | KITCHEN | [13 empty] | 1 | 1000 |  | 1 |  | REFRIGERATOR (SWB 9) |  |  | 1
| 4P | 3 | 1B | 20 | 4 | 4 | KITCHEN |  |  |  |  | 2 | [9 empty] | 200 |  |  | 0.4 | RING CKT |  |  | 0.4
| 30mA | 4 | 2R | 20 | 4 | 4 | KITCHEN |  |  |  |  | 1 | [9 empty] | 200 | 0.2 |  |  | EXISTING (SPA 7) |  |  | 0.2
|  | 5 | 2Y | 20 | 4 | 4 | KITCHEN | [9 empty] | 1 |  |  |  |  | 1500 |  | 1.5 |  | OVEN (SWK 13) |  |  | 1.5
|  | 6 | 2B | 20 | 4 | 4 | KITCHEN |  |  |  |  | 1 | [9 empty] | 200 |  |  | 0.2 | EXISTING (SWK 9) |  |  | 0.2
|  | 7 | 3R | 20 | 4 | 4 | KITCHEN | [13 empty] | 1 | 1000 | 1 |  |  | HOOD (SWK 14) |  |  | 1
| 40A | 8 | 3Y | 20 | 6 | 6 | KITCHEN | [9 empty] | 1 |  |  |  |  | 2900 |  | 2.9 |  | OVEN (SWK 8) |  |  | 2.9
| 4P | 9 | 3B | 20 | 4 | 4 | KITCHEN / PANTRY |  |  |  |  | 2 | [9 empty] | 400 |  |  | 0.8 | EXISTING (SWK 9) |  |  | 0.8
| 30mA | 10 | 4R | 20 | 4 | 4 | KITCHEN | [13 empty] | 1 | 1000 | 1 |  |  | REFRIGERATOR (SWK 4) |  |  | 1
|  | 11 | 4Y | 20 |  |  | SPARE | [13 empty] | 1 | 400 |  | 0.4 |  | SPARE | [5 empty] | 0.4
|  | 12 | 4B | 20 | 6 | 6 | KITCHEN | [9 empty] | 1 |  |  |  |  | 2400 |  |  | 2.4 | EXPRESSO (SWB 8) |  |  | 2.4
|  | 13 | 5R | 32 | 6 | 6 | KITCHEN | [8 empty] | 1 | [5 empty] | 2400 | 2.4 |  |  | DISH WASHER (SPA 3) |  |  | 2.4
| 40A | 14 | 5Y | 20 | 4 | 4 | PANTRY | [13 empty] | 1 | 1000 |  | 1 |  | REFRIGERATOR (SPA 4) |  |  | 1
| 4P | 15 | 5B | 32 | 6 | 6 | KITCHEN | [8 empty] | 1 | [5 empty] | 3300 |  |  | 3.3 | GLASS WASHER (SWB 7) |  |  | 3.3
| 30mA | 16 | 6R | 32 | 4 | 4 | KITCHEN |  |  |  |  | 7 | [9 empty] | 200 | 1.4 |  |  | RING CKT (WITH SPA 5) |  |  | 1.4
|  | 17 | 6Y | 32 | 4 | 4 | KITCHEN |  |  |  |  | 7 | [9 empty] | 200 |  | 1.4 |  | RING CKT (WITH SWB 6) |  |  | 1.4
|  | 18 | 6B | 20 |  |  | SPARE | [13 empty] | 1 | 200 |  |  | 0.2 | SPARE | [5 empty] | 0.2
|  | 19 | 7R | 20 |  |  | SPARE | [13 empty] | 1 | 200 | 0.2 |  |  | SPARE | [5 empty] | 0.2
| 40A | 20 | 7Y | 20 | 4 | 4 | KITCHEN |  |  |  |  | 2 | [9 empty] | 200 |  | 0.4 |  | EXISTING (SWK 9) |  |  | 0.4
| 4P | 21 | 7B | 20 | 4 | 4 | KITCHEN | [13 empty] | 1 | 950 |  |  | 0.95 | BLENDER (SWB 10) & GENERAL OUTLET |  |  | 0.95
| 30mA | 22 | 8R | 20 |  |  | SPARE | [13 empty] | 1 | 600 | 0.6 |  |  | SPARE | [5 empty] | 0.6
|  | 23 | 8Y | 20 |  |  | SPARE | [13 empty] | 1 | 600 |  | 0.6 |  | SPARE | [5 empty] | 0.6
|  | 24 | 8B | 20 |  |  | SPARE | [13 empty] | 1 | 550 |  |  | 0.55 | SPARE | [5 empty] | 0.55
[27 empty] | 0 | 0 | 22.65 | 0 | 0 | 2.55
LTG.=LIGHTING,EX. FAN = EXHAUST FAN, S/O=SOCKET OUTLET,SH. S/O = SHAVER SOCKET OUTLET, W/H = WATER HEATER, H/D = HAND DRYER | [22 empty] | CONT…2
D/W=DISH WASHER, FCU=FAN COIL UNIT, CCU = COOKER CONTROL UNIT, W = WINDOW TYPE A/C & S = SPLIT TYPE A/C
CEASERS PALACE VILLA
LOAD DISTRIBUTION SCHEDULE | [26 empty] | Lighting Load | Small Power | Kitchen Loads | Water Heater | FCU | Spare
Document Number: VILLA BASEMENT 1
PROJECT: | CEASERS PALACE VILLA | [20 empty] | LOCATION : ELECTRICAL ROOM
DB No: | DB-CPV-KIT
Fed From: | LH-B1-SR1-SMDB-001 | [22 empty] | PAGE- 2
RATING | RATING | SR. | CKT | MCB | CKT | ECC | ROOM/AREA | CONNECTED LOADS/POINTS | [13 empty] | WATTS | LOAD PER CKT. |  |  | REMARKS
OF | OF | NO. | NO. | RTG | WIRE | WIRE | [15 empty] | /UNIT | KILO WATTS
INCOMER | ELCB |  |  |  | SIZE | SIZE |  | LTG. | EX. | FLEX | SH. | 13A | 32A | W/H | W/M | D/W | 15A | W | S | FCU | MISC |  | R | Y | B
|  |  |  | Amp. | mm2 | mm2 |  |  | FAN | O/L | S/O | S/O | S/O |  |  |  | S/O | A/C | A/C
80A TP ISOLATOR |  | 25 | 9R | 20 |  |  | SPARE | [13 empty] | 1 | 1000 | 1 |  |  | SPARE | [5 empty] | 1
| 40A | 26 | 9Y | 20 |  |  | SPARE | [13 empty] | 1 | 1000 |  | 1 |  | SPARE | [5 empty] | 1
| 4P | 27 | 9B | 20 |  |  | SPARE | [13 empty] | 1 | 1000 |  |  | 1 | SPARE | [5 empty] | 1
| 30mA | 28 | 10R |  |  |  | SPACE | [18 empty] | SPARE
|  | 29 | 10Y |  |  |  | SPACE | [18 empty] | SPARE
|  | 30 | 10B |  |  |  | SPACE | [18 empty] | SPARE
|  | 31 | 11R | 10 |  |  | SPARE | [13 empty] | 1 | 600 | 0.6 |  |  | SPARE | [5 empty] | 0.6
| 40A | 32 | 11Y | 10 |  |  | SPARE | [13 empty] | 1 | 600 |  | 0.6 |  | SPARE | [5 empty] | 0.6
| 4P | 33 | 11B | 10 |  |  | SPARE | [13 empty] | 1 | 600 |  |  | 0.6 | SPARE | [5 empty] | 0.6
| 100mA | 34 | 12R |  |  |  | SPACE | [18 empty] | SPARE
|  | 35 | 12Y |  |  |  | SPACE | [18 empty] | SPARE
|  | 36 | 12B |  |  |  | SPACE | [18 empty] | SPARE
CABLE SIZE : 1x4C ..35...mm2 XLPE/SWA/LSOH+ 1x1C …16..mm2 CU PVC-ECC. | [13 empty] | LOAD PER PHASE (KW) | [8 empty] | 8.8 | 10.8 | 10.4 |  | 0 | 0 | 0 | 0 | 0 | 4.8 | 30 | 18
LTG.=LIGHTING,EX. FAN = EXHAUST FAN, S/O=SOCKET OUTLET,SH. S/O = SHAVER SOCKET OUTLET, W/H = WATER HEATER, H/D = HAND DRYER, D/W=DISH WASHER | [21 empty] | TOTAL LOAD = |  |  | 30 | KW
FCU=FAN COIL UNIT, CCU = COOKER CONTROL UNIT, W = WINDOW TYPE A/C & S = SPLIT TYPE A/C | [21 empty] | DEMAND LOAD = |  |  | 18 | KW
[27 empty] | 0 | 0 | 22.65 | 0 | 0 | 7.35 | 30 | TCL
[27 empty] | 0.8 | 0.8 | 0.6 | 0.8 | 0.8 | 0.6 | 0.6 | DF
[27 empty] | 0 | 0 | 13.59 | 0 | 0 | 4.41 | 18 | MDL

## DB-CPV-M
CEASERS PALACE VILLA
LOAD DISTRIBUTION SCHEDULE | [26 empty] | Lighting Load | Small Power | Kitchen Loads | Water Heater | FCU | Spare
Document Number: VILLA MEZZANINE
PROJECT: | CEASERS PALACE VILLA | [20 empty] | LOCATION : MEZZAININE FLOOR
DB No: | DB-CPV-M
Fed From: | LH-B1-SR1-SMDB-001 | [22 empty] | PAGE-1
RATING | RATING | SR. | CKT | MCB | CKT | ECC | ROOM/AREA | CONNECTED LOADS/POINTS | [13 empty] | WATTS | LOAD PER CKT. |  |  | REMARKS
OF | OF | NO. | NO. | RTG | WIRE | WIRE | [15 empty] | /UNIT | KILO WATTS
INCOMER | ELCB |  |  |  | SIZE | SIZE |  | LTG. | EX. | FLEX | SH. | 13A | 32A | W/H | W/M | D/W | CCU | W | S | FCU | MISC |  | R | Y | B
|  |  |  | Amp. | mm2 | mm2 |  |  | FAN | O/L | S/O | S/O | S/O |  |  |  |  | A/C | A/C
40A TP ISOLATOR |  | 1 | 1R | 10 | 2.5 | 2.5 | MASTER BEDROOM HL | 7 | [13 empty] | 15-5-100 | 0.185 |  |  | LIGHTING | 0.185
| 40A | 2 | 1Y | 10 | 2.5 | 2.5 | GUEST BEDROOM 1 | 16 | [13 empty] | 15-5-100 |  | 0.3425 |  | LIGHTING | 0.3425
| 4P | 3 | 1B | 10 | 2.5 | 2.5 | GUEST BEDROOM 2 | 16 | [13 empty] | 15-5-100 |  |  | 0.3425 | LIGHTING | 0.3425
| 100mA | 4 | 2R | 10 | 2.5 | 2.5 | GUEST BATHROOM 1 | 8 | [13 empty] | 15 | 0.12 |  |  | LIGHTING | 0.12
|  | 5 | 2Y | 10 | 2.5 | 2.5 | GUEST BATHROOM 2 | 8 | [13 empty] | 15 |  | 0.12 |  | LIGHTING | 0.12
|  | 6 | 2B | 10 | 2.5 | 2.5 | CORRIDOR/FOYER/ LUGGAGE | 19 | [13 empty] | 15-5-100 |  |  | 0.405 | LIGHTING | 0.405
|  | 7 | 3R | 10 | 2.5 | 2.5 | FOYER HL | 12 | [13 empty] | 30-5-100 | 0.53 |  |  | LIGHTING | 0.53
| 40A | 8 | 3Y | 10 | 2.5 | 2.5 | QUEEN ROOM | 16 | [13 empty] | 15-5-100 |  | 0.405 |  | LIGHTING | 0.405
| 4P | 9 | 3B | 10 | 2.5 | 2.5 | QUEEN BATH ROOM | 20 | [13 empty] | 15 |  |  | 0.3 | LIGHTING | 0.3
| 100mA | 10 | 4R |  |  |  | SPACE | [15 empty] | 0 |  |  | SPARE
|  | 11 | 4Y | 10 | 2.5 | 2.5 | GUEST BATHROOM 1 | 2 | [13 empty] | 50 |  | 0.1 |  | LIGHTING | 0.1
|  | 12 | 4B | 10 | 2.5 | 2.5 | GUEST BEDROOM 2 | 2 | [13 empty] | 50 |  |  | 0.1 | LIGHTING | 0.1
|  | 13 | 5R | 10 |  |  | SPARE | [13 empty] | 1 | 200 | 0.2 |  |  | SPARE | [5 empty] | 0.2
| 40A | 14 | 5Y | 10 |  |  | SPARE | [13 empty] | 1 | 200 |  | 0.2 |  | SPARE | [5 empty] | 0.2
| 4P | 15 | 5B | 10 | 4 | 4 | QUEEN BATHROOOM | 1 | [13 empty] | 100 |  |  | 0.1 |  | 0.1
| 100mA | 16 | 6R | 10 |  |  | SPARE | [13 empty] | 1 | 200 | 0.2 |  |  | SPARE | [5 empty] | 0.2
|  | 17 | 6Y | 10 |  |  | SPARE | [13 empty] | 1 | 200 |  | 0.2 |  | SPARE | [5 empty] | 0.2
|  | 18 | 6B | 10 |  |  | SPARE | [13 empty] | 1 | 200 |  |  | 0.2 | SPARE | [5 empty] | 0.2
|  | 19 | 7R | 32 | 4 | 4 | MASTER BEDROOM HL |  |  |  |  | 4 | [9 empty] | 200 | 0.8 |  |  | RING CKT |  | 0.8
| 40A | 20 | 7Y | 32 | 4 | 4 | GUEST BEDROOM 1 |  |  |  |  | 9 | [9 empty] | 200 |  | 1.8 |  | RING CKT |  | 1.8
| 4P | 21 | 7B | 32 | 4 | 4 | GUEST BEDROOM 2 |  |  |  |  | 9 | [9 empty] | 200 |  |  | 1.8 | RING CKT |  | 1.8
| 30mA | 22 | 8R | 20 | 4 | 4 | GUEST BATHROOM 1 |  |  |  | 1 | [10 empty] | 100 | 0.1 |  |  | SHAVER |  | 0.1
|  | 23 | 8Y | 20 | 4 | 4 | GUEST BATHROOM 2 |  |  |  | 1 | [10 empty] | 100 |  | 0.1 |  | SHAVER |  | 0.1
|  | 24 | 8B | 32 | 4 | 4 | FOYER HL |  |  |  |  | 5 | [9 empty] | 200 |  |  | 1 | RING CKT |  | 1
[27 empty] | 3.05 | 5.6 | 0 | 0 | 0 | 1
LTG.=LIGHTING,EX. FAN = EXHAUST FAN, S/O=SOCKET OUTLET,SH. S/O = SHAVER SOCKET OUTLET, W/H = WATER HEATER, H/D = HAND DRYER | [22 empty] | CONT…2
D/W=DISH WASHER, FCU=FAN COIL UNIT, CCU = COOKER CONTROL UNIT, W = WINDOW TYPE A/C & S = SPLIT TYPE A/C
CEASERS PALACE VILLA
LOAD DISTRIBUTION SCHEDULE | [26 empty] | Lighting Load | Small Power | Kitchen Loads | Water Heater | FCU | Spare
Document Number: VILLA MEZZANINE
PROJECT: | CEASERS PALACE VILLA | [20 empty] | LOCATION : MEZZAININE FLOOR
DB No: | DB-CPV-M
Fed From: | LH-B1-SR1-SMDB-001 | [22 empty] | PAGE- 2
RATING | RATING | SR. | CKT | MCB | CKT | ECC | ROOM/AREA | CONNECTED LOADS/POINTS | [13 empty] | WATTS | LOAD PER CKT. |  |  | REMARKS
OF | OF | NO. | NO. | RTG | WIRE | WIRE | [15 empty] | /UNIT | KILO WATTS
INCOMER | ELCB |  |  |  | SIZE | SIZE |  | LTG. | EX. | FLEX | SH. | 13A | 32A | W/H | W/M | D/W | CCU | W | S | FCU | MISC |  | R | Y | B
|  |  |  | Amp. | mm2 | mm2 |  |  | FAN | O/L | S/O | S/O | S/O |  |  |  |  | A/C | A/C
40A TP ISOLATOR |  | 25 | 9R | 32 | 4 | 4 | QUEEN ROOM |  |  |  |  | 8 | [9 empty] | 200 | 1.6 |  |  | RING CKT |  | 1.6
| 40A | 26 | 9Y | 20 | 4 | 4 | LIFT SHAFT | [13 empty] | 1 | 1000 |  | 1 |  | LIFT |  | 1 |  |  | 1
| 4P | 27 | 9B | 32 | 4 | 4 | STORE |  |  |  |  | 3 | [9 empty] | 200 |  |  | 0.6 | RING CKT |  | 0.6
| 30mA | 28 | 10R | 20 |  |  | SPARE | [23 empty] | 0
|  | 29 | 10Y | 20 |  |  | SPARE | [23 empty] | 0
|  | 30 | 10B | 20 | 4 | 4 | QUEEN BATHROOM |  |  |  | 1 | [10 empty] | 100 |  |  | 0.1 | SHAVER |  | 0.1
|  | 31 | 11R | 20 |  |  | SPARE | [13 empty] | 1 | 200 | 0.2 |  |  | SPARE | [5 empty] | 0.2
| 40A | 32 | 11Y | 20 | 4 | 4 | BACK OF HOUSE CORRIDOR | [12 empty] | 1 |  | 300 |  | 0.3 |  | A/C |  |  |  |  | 0.3
| 4P | 33 | 11B | 20 |  |  | SPARE | [13 empty] | 1 | 400 |  |  | 0.4 | SPARE | [5 empty] | 0.4
| 100mA | 34 | 12R | 20 | 4 | 4 | GUEST BEDROOM 2 | [12 empty] | 1 |  | 300 | 0.3 |  |  | A/C |  |  |  |  | 0.3
|  | 35 | 12Y | 20 | 4 | 4 | BACK OF HOUSE CORRIDOR | [12 empty] | 1 |  | 300 |  | 0.3 |  | A/C |  |  |  |  | 0.3
|  | 36 | 12B | 20 |  |  | SPARE | [13 empty] | 1 | 200 |  |  | 0.2 | SPARE | [5 empty] | 0.2
|  | 37 | 13R | 20 |  |  | SPARE | [13 empty] | 1 | 250 | 0.25 |  |  | SPARE | [5 empty] | 0.25
| 40A | 38 | 13Y | 20 | 4 | 4 | GUEST BEDROOM 1 | [12 empty] | 1 |  | 300 |  | 0.3 |  | A/C |  |  |  |  | 0.3
| 4P | 39 | 13B | 20 |  |  | SPARE | [13 empty] | 1 | 400 |  |  | 0.4 | SPARE | [5 empty] | 0.4
| 30mA | 40 | 14R | 32 |  |  | SPARE | [13 empty] | 1 | 1000 | 1 |  |  | SPARE | [5 empty] | 1
|  | 41 | 14Y | 20 |  |  | SPARE | [13 empty] | 1 | 200 |  | 0.2 |  | SPARE | [5 empty] | 0.2
|  | 42 | 14B | 20 |  |  | SPARE | [13 empty] | 1 | 200 |  |  | 0.2 | SPARE | [5 empty] | 0.2
|  | 43 | 15R |  |  |  | SPACE | [15 empty] | 0
|  | 44 | 15Y |  |  |  | SPACE | [16 empty] | 0 | [7 empty] | 0
|  | 45 | 15B |  |  |  | SPACE | [17 empty] | 0
|  | 46 | 16R |  |  |  | SPACE | [15 empty] | 0
|  | 47 | 16Y |  |  |  | SPACE | [16 empty] | 0
|  | 48 | 16B |  |  |  | SPACE | [17 empty] | 0
CABLE SIZE : 1x4C ..16....mm2 XLPE/SWA/LSOH+ 1x1C …16...mm2 CU PVC-ECC. | [13 empty] | LOAD PER PHASE (KW) | [8 empty] | 5.485 | 5.3675 | 6.1475 |  | 0 | 3.3 | 0 | 0 | 2.2 | 2.85 | 18 | 14.4
LTG.=LIGHTING,EX. FAN = EXHAUST FAN, S/O=SOCKET OUTLET,SH. S/O = SHAVER SOCKET OUTLET, W/H = WATER HEATER, H/D = HAND DRYER, D/W=DISH WASHER | [21 empty] | TOTAL LOAD = |  |  | 17 | KW
FCU=FAN COIL UNIT, CCU = COOKER CONTROL UNIT, W = WINDOW TYPE A/C & S = SPLIT TYPE A/C | [21 empty] | DEMAND LOAD = |  |  | 14.4 | KW
[27 empty] | 3.05 | 8.9 | 0 | 0 | 2.2 | 3.85 | 18 | TCL
[27 empty] | 0.8 | 0.8 | 0.6 | 0.8 | 0.8 | 0.8 | 0.8 | DF
[27 empty] | 2.44 | 7.12 | 0 | 0 | 1.76 | 3.08 | 14.4 | MDL