## SMDB-TWS-L09.12-02
Project: |  | CEASARS PALACE VILLA | [6 empty] | Owner: | Dubai Holding Hospitality Asset |  | Area: Bluewaters, Dubai, UAE.
Planned Completion Date: | [8 empty] | Consultant: Aurecon |  |  | Plot No.:
Panel Reference |  | LH-B1-SR1-SMDB-001 | [9 empty] | Loc. of Panel: |  | Electrical Cabinet @ Basement Level
Circuit/Feeder DB No. |  | Single / Three Phase | Rating (Amps) |  |  | Fault Duty (kA) | XLPE / SWA / LSF | Earth leak Protection ELR / ELCB (mA) | Cable Size |  |  | Connected Load |  |  |  |  | Proposed Type and No. of kWh Meters |  |  |  | Remarks
|  |  | F/S ISOL | MCCB | MCB |  |  |  | 2x1c / 4x1c mm2 | 2c, 3c, 4c mm2 | ECC mm2 | R-Ph (kW) | Y-Ph (kW) | B-Ph (kW) | TCL (kW) | MDL (kW) | 1-Ph (1) | 3-Ph (2) | 3-Ph (3) | LV/HV CT (4)
INCOMER (NON AUTO) : |  | 3 |  | 500 N/A |  | 35 | XLPE/SWA/LSF | 400000 |  | 2 x 4C 240 | 2 x 1c 120mm² | 75.8183 | 79.6544 | 79.6284 | 235.1012 | 179.217
OUTGOING WAY :
1) | CP-ODU (20A TPN ISOLATOR) | 3 |  | 25 |  | 35 | XLPE/SWA/LSF |  |  | 1 x 4c 16mm² | 1 x 1c 16mm² | 2.5667 | 2.5667 | 2.5667 | 7.7 | 6.16 |  |  |  |  | 100 mA ELCB
2) | DB-CPV-MAJ | 3 |  | 100 |  | 35 | XLPE/SWA/LSF |  |  | 1 x 4c 95mm² | 1 x 1c 50mm² | 13.3 | 15.485 | 14.59 | 43.375 | 31.422
3) | CP-SWIMMING POOL (63A TPN ISOLATOR) | 3 |  | 63A |  | 35 | XLPE/SWA/LSF |  |  | 1 x 4c 50mm² | 1 x 1c 25mm² | 9 | 9 | 9 | 27 | 21.6 |  |  |  |  | ELCB + STARTER WITHIN CONTROL PANEL
4) | DB-CPV-M | 3 |  | 40 |  | 35 | XLPE/SWA/LSF |  |  | 1 x 4c 16mm² | 1 x 1c 16mm² | 5.485 | 5.3675 | 6.1475 | 17 | 14.4
5) | CP-WATER FEATURE (40A TPN ISOLATOR) | 3 |  | 40A |  | 35 | XLPE/SWA/LSF |  |  | 1 x 4c 16mm² | 1 x 1c 16mm² | 3.3333 | 3.3333 | 3.3333 | 10 | 8 |  |  |  |  | ELCB + STARTER WITHIN CONTROL PANEL
6) | CP-JACUZZI (40A TPN ISOLATOR) | 3 |  | 40A |  | 35 | XLPE/SWA/LSF |  |  | 1 x 4c 16mm² | 1 x 1c 16mm² | 4 | 4 | 4 | 12 | 9.6 |  |  |  |  | ELCB + STARTER WITHIN CONTROL PANEL
7) | FEEDER PILLAR -01 | 3 |  | 40 |  | 35 | XLPE/SWA/LSF |  |  | 1 x 4c 25mm² | 1 x 1c 16mm² | 4.3667 | 4.3667 | 4.3667 | 13.1 | 10.48 |  |  |  |  | Existing Panel (Not in Scope).
8) | FEEDER PILLAR -02 | 3 |  | 40 |  | 35 | XLPE/SWA/LSF |  |  | 1 x 4c 16mm² | 1 x 1c 16mm² | 2.6333 | 2.6333 | 2.6333 | 7.9 | 6.32 |  |  |  |  | Existing Panel (Not in Scope).
9) | DB-CPV-KIT | 3 |  | 80 |  | 35 | XLPE/SWA/LSF |  |  | 1 x 4c 35mm² | 1 x 1c 16mm² | 8.8 | 10.8 | 10.4 | 30 | 18
10) | DB-CPV-B1 | 3 |  | 63 |  | 35 | XLPE/SWA/LSF |  |  | 1 x 4c 16mm² | 1 x 1c 16mm² | 10 | 9.7686 | 10.2576 | 30.0012 | 23.635
11) | CP-SPLASH (40A TPN ISOLATOR) | 3 |  | 40 |  | 35 | XLPE/SWA/LSF |  |  | 1 x 4c 16mm² | 1 x 1c 16mm² | 3.3333 | 3.3333 | 3.3333 | 10 | 8 |  |  |  |  | ELCB + STARTER WITHIN CONTROL PANEL
12) | INDUCTION COOKTOP (32A TPN ISOLATOR) | 3 |  | 40 |  | 35 | XLPE/SWA/LSF |  |  | 1 x 4c 16mm² | 1 x 1c 16mm² | 3.6667 | 3.6667 | 3.6667 | 11 | 8.8
13) | INDUCTION COOKTOP (32A TPN ISOLATOR) | 3 |  | 40 |  | 35 | XLPE/SWA/LSF |  |  | 1 x 4c 16mm² | 1 x 1c 16mm² | 3.6667 | 3.6667 | 3.6667 | 11 | 8.8
14) | CP-LIFT (20A TPN ISOLATOR) | 3 |  | 20 |  | 35 | XLPE/SWA/LSF |  |  | 1 x 4c 16mm² | 1 x 1c 16mm² | 1.6667 | 1.6667 | 1.6667 | 5 | 4 |  |  |  |  | ELR
FED FROM:
LH-B2-LV-MDB-03 | [5 empty] | TOTAL CONNECTED LOAD PER PHASE | [5 empty] | 75.8183 | 79.6544 | 79.6284 | 235.0762 | 179.217 | 0 | 0 | 0 | 0
MAXIMUM DEMAND (3 Phase): |  |  | 179.217 |  | kW at | 0.76238 | DIVERSITY | [5 empty] | TOTAL CONNECTED LOAD (3 Phase): | 235.0762 |  |  | kW
[20 empty] | REV. : | 01
[20 empty] | DATE : | 2022-03-17

## Template1 (hidden)
Project: | [10 empty] | Owner:
Job No.:
Planned Completion Date: | [7 empty] | Consultant: |  |  | Plot No.:
| SUB MAIN DISTRIBUTION BOARD SCHEDULE | [9 empty] | Prepared by: |  |  |  |  | Checked by:
Panel Reference | [10 empty] | Loc. of Panel:
Circuit/Feeder DB No. | Single / Three Phase | Rating (Amps) |  |  | Fault Duty (kA) | LSZH or XLPE / SWA / LSZH | Earth leak Protection ELR / ELCB (mA) | Cable Size No. in Parallel x mm² |  |  | Connected Load |  |  |  | Proposed Type and No. of kWh Meters |  |  |  | Remarks
|  | F/S ISOL | MCCB | MCB |  |  |  | 2x1c / 4x1c mm2 | 2c, 3c, 4c mm2 | ECC mm2 | L1-Ph (kW) | L2-Ph (kW) | L3-Ph (kW) | TCL (kW) | 1-Ph (1) | 3-Ph (2) | 3-Ph (3) | LV/HV CT (4)
INCOMER : (NON AUTO) | [13 empty] | 0
OUTGOING WAY :
0
FED FROM:
[5 empty] | TOTAL CONNECTED LOAD PER PHASE | [5 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
MAXIMUM DEMAND (3 Phase): |  | 0 |  | kW at |  | DIVERSITY | [5 empty] | TOTAL CONNECTED LOAD (3 Phase): | 0 |  | kW |  |  | SHEET :
REV. :
DATE :